## Slave address
S332 holding register table
Communication: | [RS485]
Protocol: | [Modbus]
Slave address: | [1]
Baud rate: | [19200]
Interframe spacing char: | [0]
Interframe spacing US: | [0]
Response delay: | [0]
Response timeout(s): | [10]
Return error value: | [-9999]
Measurement point | Sensor | Channel | Address | Data type | No. of byte | Unit | Resolution | Func code
EX/XA2 | S461_Flow_Meter | Flow | 0 | FLOAT_L | 4 | m3/h | 0.1 | 3
EX/XA2 | S461_Flow_Meter | Velociticy | 2 | FLOAT_L | 4 | m/s | 0.01 | 3
EX/XA2 | S461_Flow_Meter | Consumption | 4 | FLOAT_L | 4 | m3 | 0.1 | 3
-/- | S461_Flow_Meter | Consumption (R) | 6 | FLOAT_L | 4 | m3 | 0.1 | 3
-/- | S461_Flow_Meter | Signal Quality | 8 | UINT32_L | 4 |  | 1 | 3
-/- | S040 | Temperature | 10 | FLOAT_L | 4 | ℃ | 0.1 | 3
EX2/XA2 | S040 | Humidity | 12 | FLOAT_L | 4 | %RH | 0.1 | 3
-/- | S040 | Pressure | 14 | FLOAT_L | 4 | kPa | 0.1 | 3
-/- | S132 | 0.1 < d ≤ 0.5 um | 16 | FLOAT_L | 4 | cn/m3 | 1 | 3
EX2/XA2 | S132 | 0.5 < d ≤ 1.0 um | 18 | FLOAT_L | 4 | cn/m3 | 1 | 3
-/- | S132 | 1.0 < d ≤ 5.0 um | 20 | FLOAT_L | 4 | cn/m3 | 1 | 3
-/- | S132 | d > 5.0 um | 22 | FLOAT_L | 4 | cn/m3 | 1 | 3
EX/XA2 | S217 | Temperature | 24 | FLOAT_L | 4 | ℃ | 0.1 | 3
EX/XA2 | S217 | Relative humidity | 26 | FLOAT_L | 4 | % | 0.001 | 3
EX/XA2 | S217 | Pressure dew point | 28 | FLOAT_L | 4 | ℃td | 0.1 | 3
-/- | S217 | Atmosphere dew point | 30 | FLOAT_L | 4 | ℃td atm | 0.1 | 3
-/- | S217 | Mixing ratio | 32 | FLOAT_L | 4 | g/kg | 0.001 | 3
-/- | S217 | Absolute humidity | 34 | FLOAT_L | 4 | g/m3 | 0.01 | 3
-/- | S217 | Volume ration | 36 | FLOAT_L | 4 | ppm | 0.01 | 3
-/- | S600 | Dew point | 38 | FLOAT_L | 4 | ℃td | 0.1 | 3
-/- | S600 | Oil | 40 | FLOAT_L | 4 | ppm | 0.1 | 3
S605/XA | S605 | O2 | 42 | FLOAT_L | 4 | % | 0.1 | 3
S605/XA | S605 | CO2 | 44 | FLOAT_L | 4 | PPM | 0.1 | 3
S605/XA | S605 | CO | 46 | FLOAT_L | 4 | PPM | 0.1 | 3
EX2/XA2 | Virtual Sensor | co+co2 | 48 | FLOAT_L | 4 | ppm | 0.1 | 3
-/- | Virtual Sensor | Test relay | 50 | FLOAT_L | 4 | m | 0.1 | 3
EX2/XA2 | Current | 020 | 52 | FLOAT_L | 4 | mA | 1 | 3
-/- | Voltage | 545 | 54 | FLOAT_L | 4 | V | 1 | 3
Info: Use this holding register table to read data from the S332 via Modbus/RTU or Modbus/TCP